Pathology and Laboratory Medicine Service Contingency Plan

Revised 6/18/2019

| Pathology and Laboratory Medicine Service Contingency Plan |  |  |  |  |
| --- | --- | --- | --- | --- |
| Prepared by: | Lee Ann Speaks |  | Authorized by: | Dr. Bonnie Mitchell |
| Title: | Lab Safety Officer |  | Title: | Chief PLMS |
| Date Prepared: | 11/29/2006 |  | Date Authorized: | 11/26/2006 |
| Revised by: | Vicki B. Richardson |  |  |  |
| Title: | P&LMS Safety Officer |  |  |  |
| Date Revised: | 3/1/2013 |  |  |  |
| Review Authority: | Chief PLMS |  |  |  |
| Review Authority: | Lab Safety Officer |  |  |  |
| Reviewed (Date) | By |  | Revised (Date) | By |
| 11/29/2006 | Lee Ann Speaks |  | 11/29/2006 | Lee Ann Speaks |
| 11/29/2006 | Dr. Bonnie Mitchell |  | 12/14/2007 | Lee Ann Speaks |
| 12/14/2007 | Lee Ann Speaks |  | 9/15/2008 | Lee Ann Speaks |
| 12/21/2007 | Dr. Bonnie Mitchell |  | 6/2/2009 | Vicki B. Richardson |
| 9/15/2008 | Lee Ann Speaks |  | 6/17/2010 | Vicki B. Richardson |
| 9/15/2008 | Dr. Bonnie Mitchell |  | 6/16/2011 | Vicki B. Richardson |
| 2/27/2009 | Dr. Bonnie Mitchell |  | 3/7/2012 | Vicki B. Richardson |
| 6/2/2009 | Vicki B. Richardson |  | 3/1/2013 | Vicki B. Richardson |
| 6/8/2009 | Dr. Bonnie Mitchell |  | 3/11/2014 | Vicki B. Richardson |
| 6/17/2010 | Vicki B. Richardson |  | 5/15/2015 | Vicki B. Richardson |
| 6/17/2010 | Dr. Bonnie Mitchell |  | 8/31/2015 | Vicki B. Richardson |
| 6/16/2011 | Vicki B. Richardson |  | 5/9/2016 | Vicki B. Richardson (Minor changes) |
| 6/16/2011 | Dr. Bonnie Mitchell |  | 7/19/2017 | Chip Logan (Minor changes) |
| 3/7/2012 | Vicki B. Richardson |  | 10/16/2018 | Chip Logan (Minor Changes) |
| 3/7/2012 | Dr Luis Samayoa |  | 6/18/2019 | Chip Logan (Minor Changes) |
| 8/28/2012 | Dr. David Hunt |  |  |  |
| 3/1/2013 | Vicki B Richardson |  |  |  |
| 3/1/2013 | Dr. David Hunt |  |  |  |
| 3/11/2014 | Dr. David Hunt |  |  |  |
| 5/15/2015 | Dr. David Hunt |  |  |  |
| 8/31/2015 | Vicki B. Richardson |  |  |  |
| 5/9/2016 | Vicki B. Richardson |  |  |  |
| 12/14/17 | Dr. Laura Crump, MD |  |  |  |
| 7/19/2017 | Chip Logan |  |  |  |
| 10/16/2018 | Chip Logan |  |  |  |
| 6/18/2019 | Chip Logan |  |  |  |

DATE:     June 18, 2019

FUNCTIONAL UNIT:  P&LMS:  Ancillary Testing CD & LD	 		FUNCTIONAL UNIT MANAGER:  Susan Thompson

| Mission Critical System | - Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | OK with emergency lighting | Engineering service | - Flashlights - Have fresh batteries on hand | Determine extent of outage. | Use flashlights |
| 2. Electrical Power (Generator Power Available) | OK with emergency power. Loss of both normal and emergency power would result in inability to test. | N/A | Use extension cords to connect equipment to keep Tests can be sent to main lab if lab operational. | 1. Length of downtime 2. Alternate lab to use | Send testing to main laboratory if available |
| 3. Steam Distribution | N/A | N/A | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | N/A | N/A | N/A | N/A | N/A |
| 5. Room or Hood Exhaust | N/A | N/A | N/A | N/A | N/A |
| 6. Water Delivery | 1. Lack of hand washing. |  | - Use antibacterial hand cleanser. | N/A | N/A |
| 7. Water Conditioning Or Drinkability | N/A | Engineering Service | N/A | Water quality | Inform staff to drink bottled water – not tap water. |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Biohazard waste will accumulate. | Engineering Service | Biohazardous waste accumulation would be minimal. | Determine extent of outage. | Contact engineering for help with biohazard waste disposal. |
| 9. Critical Supplies | Lack of reagents results in inability to perform testing. | Supply Office | Stockpile of reagents on hand. | Inventory of reagents | 1. Reduce to critical tests only. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | N/A testing done at point of care | Office of Information & Technology (OI&T) |  | N/A | N/A |
| 11. VISTA & Other Computer Applications | Delay of results to chart | Laboratory Information Manager (LIM) | Backup procedures are in place. | Assess length of downtime. | - Activate established computer downtime procedures |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Lack of notification |  | Alert staff. | Listen to intercom for fire announcements. | - Manually monitor temperatures of refrigerators and freezers - Inform staff |
| 13. Elevators & Other Vertical Transport | N/A |  | Use stairs | Determine extent of outage. | Use stairs |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | N/A | Engineering Service |  |  |  |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | NA |  |  |  |  |

DATE: June 18, 2019

FUNCTIONAL UNIT:  P&LMS:  Histopathology 				FUNCTIONAL UNIT MANAGER:  Kim Manuel

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Without lights, staff cannot carry out their duties. | Safety Officer | 1. Have flashlight with batteries. 2. Be familiar with egress routes. | 1. Determine extent of outage. | Use flashlights |
| 2. Electrical Power (Generator Power Available) | Unable to perform duties without emergency power. | Safety Officer | Use extension cords to connect critical equipment to emergency power outlets. | Determine extent of outage. | If emergency power unavailable, may be required to shift to outside lab (UK). |
| 3. Steam Distribution | N/A | N/A | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Could only work so long without heat or HVAC due to staff safety. | Engineering Service |  | Determine extent of outage. | Request fans from engineering |
| 5. Room or Hood Exhaust | Would need Safety evaluation before proceeding with regular duties. | Safety Officer and Engineering Service | Try to perform duties with minimal chemical requirements. | Evaluation by Safety Officer to access danger from chemical fumes. | Do not process until situation is determined safe by hospital safety office. |
| 6. Water Delivery | 1. Water required for all staining functions. 2. Hand washing critical. | Safety Officer and Engineering Service | - Small inventory of water kept on hand. - Use antibacterial hand cleanser. | Assess extent of outage. | Inventory of lab wide water supply to determine staining capabilities. |
| 7. Water Conditioning Or Drinkability | Minimal impact | Engineering Service | If emergency power and water is available, we may use reagent grade water from our water purification system. | Inform staff | Report to Safety Officer or Engineering Service |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Cannot flush chemicals (stains) without H2O | Engineering Service | Store biohazard waste until able to dispose of per procedure. | Inform staff |  |
| 9. Critical Supplies | Without supplies, cannot operate. | Purchasing | Stock pile approx. 2 week inventory. | Inventory supplies | May borrow supplies from UK. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Minimal impact Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | Have all required materials on hand (supplies). Landline located in blood bank above bench 20 and 21 | Assess situation, inform staff. | Have all required materials on hand. |
| 11. VISTA & Other Computer Applications | Cannot log in or report electronically An interruption in VISTA operations would interrupt order entry and results reporting. An interruption in VISTA operations would interrupt order entry and results reporting. Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | Establish back-up system for logging in and reporting results. - Establish back-up systems for processing pathology and laboratory requests and inputting exam results into the Vista system. 2. Landline located in blood bank above bench 20 and 21 | Inquire of OI&T about length of down time. | Use handwritten tissue examination forms that can be entered into VistA later. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | All alarms required for assessing situation | Engineering Service | Alert staff | 1. Inform staff. 2. Listen for intercom announcement. | 1. Contact Engineering Service to make necessary repairs. 2. Monitor temperatures manually |
| 13. Elevators & Other Vertical Transport | Minimal impact except to secure specimens | Engineering Service | 1. Use stairways | Keep staff informed. | Inform of egress route to secure specimens. |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | N/A | N/A | N/A | N/A | N/A |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | NA | N/A | N/A | N/A | N/A |

FUNCTIONAL UNIT:  P&LMS:  Cytology								DATE:     June 18, 2019

FUNCTIONAL UNIT MANAGER:  Derek Hensley

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Without lights, minimal duties performed. | Safety Office | Stock flashlights with fresh batteries | Determine extent of outage. | May relocate necessities to area with better lighting. |
| 2. Electrical Power (Generator Power Available) | Without power, minimal duties performed. | Safety Office | Use extension cords to connect critical equipment to emergency power outlets. Cytology Section refrigerator is on emergency power. | Determine extent of outage. | 1. May need to centrifuge specimens in another area. 2. Specimens can be stored for a short amount of time. (<1 week). |
| 3. Steam Distribution | N/A | N/A | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Could only work so long without heat or air conditioning due to staff safety. | Engineering Service | N/A | Determine extent of outage. | Request fans from engineering |
| 5. Room or Hood Exhaust | Minimal Impact | Safety Office |  | Determine how long without exhaust | None |
| 6. Water Delivery | 1. Hand washing critical. 2. Water required for staining. | Safety Office | 1. Use antibacterial hand cleanser. 2. Use bottled water for staining. | 1. Determine how long without H2O. 2. Inventory lab wide water supply. | 1. Use antibacterial hand cleanser. 2. Use bottled water for staining. |
| 7. Water Conditioning Or Drinkability | Minimal impact except for drinking water. | Chief Medical Technologist | If emergency power is available and water is available, we may use reagent grade water from our water purification system. | Minimize use of water. |  |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Unable to dispose of biohazard waste. | Safety Office | Stock extra biohazard bags. |  | 1. Cytology has minimal biohazard waste. 2. Store in designated waste room for disposal by engineering. |
| 9. Critical Supplies | Unable to perform FNAs, process, and stain. | Purchasing | Stockpile reagents for approx. 2 weeks. | Determine which procedures to perform. | 1. Stockpile reagents. 2. Could possible borrow supplies from UK. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Unable to communicate with medical staff concerning FNAs Would need to use landline phone for communication. All other phones are dependent on internet connection. | 1. Chief, OI&T 2. Chief, Security | Check with OI&T about back-up. Landline located in blood bank above bench 20 and 21 | Check to see if any FNAs scheduled. | Can walk to CT Scan & Ultrasound to check on scheduled FNAs. |
| 11. VISTA & Other Computer Applications | Reporting results delays An interruption in VISTA operations would interrupt order entry and results reporting. | LIM | Establish backup system. | Check with LIM about length of downtime. | Cytology has manual back-up system. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Needed to alert staff of a fire | Safety Manager | Test alarms | 1. Inform staff. 2. Listen to intercom for fire announcements. | Contact lab safety officer. |
| 13. Elevators & Other Vertical Transport | Minimal Impact | Engineering Service | Use stairways | Keep informed | Know egress route to secure specimens |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Minimal Impact | Engineering Service | N/A | N/A | Would rely upon physical transport of specimens. |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | NA | N/A | N/A | N/A | N/A |

P&LMS Contingency Plan

DATE:     June 18, 2019

FUNCTIONAL UNIT:  P&LMS:  Chemistry	                                            FUNCTIONAL UNIT MANAGER:  Lee Ann Speaks

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | OK with emergency lighting | N/A | - Flashlights - Have fresh batteries on hand | Determine extent of outage. | Use flashlights |
| 2. Electrical Power (Generator Power Available) | OK with emergency power. Loss of both normal and emergency power would result in closure of section. | N/A | Use extension cords to connect critical equipment and water purification system to emergency power outlets. Set up list to send all tests elsewhere (Lab Corp) | 1. Length of downtime 2. Alternate lab to use | Send testing to alternate laboratory |
| 3. Steam Distribution | N/A | N/A | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Analyzers will overheat in time |  |  | - Determine extent of outage. - Temperature | - Turn off analyzers. - Request fans from engineering to help cool instruments. |
| 5. Room or Hood Exhaust | Minimal Impact | Safety Office |  | Fumes | Wear mask when pouring acids. |
| 6. Water Delivery | 1. Minimal water requirements for testing. 2. Lack of hand washing. |  | - Utilize carboys for deionized water for testing/dilutions. - Use antibacterial hand cleanser. | Inventory deionized water. | Prioritize testing requirements. |
| 7. Water Conditioning Or Drinkability | Minimal Impact | Engineering Service | If emergency power is available and water is available, we may use reagent grade water from our water purification system. | Water quality | Inform staff to drink bottled water – not tap water. |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Can’t dispose of 24 hr. urines thru sinks. Lack of disposal of specimens would create large amount quickly | Engineering Service | Could store urine containers in biohazard waste room to await disposal. | Determine extent of outage. | Contact engineering for help with biohazard waste disposal. |
| 9. Critical Supplies | Lack of reagents results in inability to perform testing. | Supply Office | Stockpile of reagents on hand. | Inventory of reagents | 1. $ to send out? 2. Reduce to critical tests only. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Unable to communicate critical values Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | Landline located in blood bank above bench 20 and 21 | Determine extent of outage. | 1. Walk results to area. |
| 11. VISTA & Other Computer Applications | Major Impact 1. An interruption in VISTA operations would interrupt order entry and results reporting. 2. Would need to use landline phone for communication. All other phones are dependent on internet connection. | LIM | Backup procedures are in place. | Assess length of downtime. | - Activate established computer downtime procedures - Walk results, backup slips, etc. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Lack of notification |  | Alert staff. | Listen to intercom for fire announcements. | - Manually monitor temperatures of refrigerators and freezers - Inform staff |
| 13. Elevators & Other Vertical Transport | N/A |  | Use stairs | Determine extent of outage. | Use stairs |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Loss of pneumatic tube would cause delay in specimen delivery | Engineering Service |  | Determine extent of outage. | Walk specimens. |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | NA |  |  |  |  |

DATE:    June 18, 2019

FUNCTIONAL UNIT:  P&LMS: Microbiology	 		                     FUNCTIONAL UNIT MANAGER:  Baker Burke

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | OK with emergency power. Loss of both normal and emergency power would result in closure of section. |  | - Flashlights - Have fresh batteries on hand | Determine extent of outage. | - Use flashlights - Send patient testing to LabCorp |
| 2. Electrical Power (Generator Power Available) | The loss of the primary source would have little effect on the functioning of the laboratory. Most of the instruments required for testing are on emergency power outlets. (See Prep. column).However, if both sources of electricity were lost, this would result in total shutdown of all testing procedures. All instruments should be shutdown to prevent damage by surges when power is restored. We would be able to collect specimens to be sent to another laboratory. |  | - Use extension cords to connect critical equipment and water purification system to emergency power outlets. - The triple refrigerator storing media is not on emergency power. Media could be moved to walk-in refrigerator. The Microscan Walkaway is connected to a direct critical power circuit. No extension cords needed. | Determine extent of outage. | - Move media to functioning refrigerator - Send patient testing to LabCorp |
| 3. Steam Distribution | N/A |  | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Equipment may overheat | Engineering Service | Request fans from engineering to help cool area/instrumentation. | Determine extent of outage. | - Evaluate to protect equipment. - Request fans from engineering to help cool area |
| 5. Room or Hood Exhaust | Potential for germ spread contamination in positive pressure rooms/hoods | Safety Office Chief Technologist | Plating of specimens (except respiratory specimens and specimens sent for TB and fungus evaluation) would continue on countertop using universal precautions. | Determine extent of outage. | - Call patient’s provider if exams cannot be performed due to loss of exhaust capabilities. - Enter electronic work order. |
| 6. Water Delivery | Water required for some tests. Hand washing critical | Safety Office | 1. Keep 5 gallon container of deionized water available. 2. Use antibacterial hand cleanser. | Determine extent of outage. | - Have stored water on hand. - Use antibacterial hand cleanser. |
| 7. Water Conditioning Or Drinkability | Minimal impact except for drinking water | Supply Officer | If emergency power is available and water is available, we may use reagent grade water from our water purification system. | Water quality | Report failure to Engineering Service. |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Unable to dispose of biohazard waste | Safety Office | Stock extra biohazard bags and containers. | Ability to preserve staff safety and environmental controls | Contact environmental management for assistance with disposal. |
| 9. Critical Supplies | Adverse affect on the operations of the pathology and laboratory department. | Chief, Purchasing and Contracting Chief Technologist | Stock enough supplies to cover at least 2 weeks. | Evaluate the situation and determine which studies can be performed. | - Notify COS and Site Manager of which studies can be performed and which are no longer available. - Contact nearby hospital to check on their supplies |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Loss of phones will impede the department’s ability to communicate with medical center staff and external contacts Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | Landline located in blood bank above bench 20 and 21 | Determine extent of outage | - Communicate urgent results via hand delivery of report to appropriate area. - If computer is working- communicate via e-mail. |
| 11. VISTA & Other Computer Applications | 1. An interruption in VISTA operations would interrupt order entry and results reporting. | OI&T | Establish back-up systems for processing pathology and laboratory requests and inputting exam results into the Vista system. | Wait for word from IRM as to the length of the downtime | - Start using VA Lab Slips; distribute to wards. - At reception desk begin manual logs and log sheets for each exam - Use runners for inpatient results. Call MD if critical results. - After Vista is restored, enter all exams into system. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Fire alarms needed to alert staff of a fire | Chief, Security |  | Determine extent of outage | - Notify staff. - Remain alert for notification on the fire alarm via intercom system - Manually monitor refrigerator, incubator and freezer temperatures |
| 13. Elevators & Other Vertical Transport | Minimal Impact |  |  |  |  |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Delay in specimen testing/reporting. | Engineering Service |  | Determine extent of outage | Physically walking specimens. |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | No Impact |  |  |  |  |

DATE:      June 18, 2019

FUNCTIONAL UNIT:  P&LMS: Hematology	 	                                    FUNCTIONAL UNIT MANAGER:  Susan Buchanan

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Emergency lights available in coagulation/urinalysis section only. | Safety Office Engineering Service | 1. Staff should be informed. 2. Flashlights are available. 3. Staff informed where the flashlights are located. | Determine extent of outage, is it contained or throughout the service? | Use flashlight or emergency lights. |
| 2. Electrical Power (Generator Power Available) | 1. No primary power. 2. May cause potential damage to the electronics of the equipment used. | Safety Office Engineering Service | - Use extension cords to connect critical equipment and water purification system to emergency power outlets. - All Hematology equipment is on emergency power. - Confirm contingency plans with UK or outside reference labs. | Service chief to determine the extent of the outage and the projected length of the outage | If emergency power won’t come on, may shift testing to the reference lab. |
| 3. Steam Distribution | N/A | N/A | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | 1. Loss of heat and AC could impact operations to the staff. 2. Overheating could cause damage to the electronic equipment. | Chief, Engineering Service, Bio-Medical | Fans and heaters may be acquired from Engineering to ensure operation of equipment. | Service chief to determine the extent of the outage and projected length of the outage. | - Evaluate situation to protect equipment (possible shutdown). - Restart equipment after cool off. - Send tests out - Fans and heaters may be acquired from Engineering to ensure operation of equipment |
| 5. Room or Hood Exhaust | Minimal Impact | Safety Office Chief Technologist |  | Determine the extent of the outage. | Place work order. |
| 6. Water Delivery | 1. Water required for stainer. 2. Flush sinks 3. Hand washing critical 4. Used in millipore filter system | Safety Office | 1. 5 gallon deionized water kept on hand for backup. Small amount needed for stainer. 2. Use antibacterial hand cleanser. | Determine the extent of the outage. | Have stored water on hand. Switch to unconcentrated cellpack. |
| 7. Water Conditioning Or Drinkability | Minimal impact except for drinking water | Supply Officer | If emergency power is available and water is available, we may use reagent grade water from our water purification system. |  |  |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Unable to dispose of biohazard waste | Safety Office | Stock extra red bags and containers. | Ability to preserve staff safety and environmental controls | 1. Contact environmental management for assistance with disposal |
| 9. Critical Supplies | Adverse affect on the operations of the pathology and laboratory department. | Chief, Purchasing and Chief Technologist | Stock enough supplies to cover at least 2 weeks. | Evaluate the situation and determine which studies can be performed. | 1. Notify COS and Site Manager of which studies can be performed and which are no longer available. 2. Contact nearby hospital to check on their supplies |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Loss of phones will impede the department’s ability to communicate with medical center staff and external contacts Would need to use landline phone for communication. All other phones are dependent on internet connection. | Chief, OI&T Chief, Security | Landline located in blood bank above bench 20 and 21 | 1. Inability to communicate critical values. | 1. Physically walk results to clinic areas. |
| 11. VISTA & Other Computer Applications | 1. An interruption in VISTA operations would interrupt order entry and results reporting. | OI&T | Establish back-up systems for processing pathology and laboratory requests and inputting exam results into the Vista system. | Wait for word from OI&T as to the length of the downtime | - Start using VA Lab Slips; distribute to wards. - At reception desk begin manual logs and log sheets for each exam - Use runners for inpatient results. Call MD if critical results or urgent for outpatients. - After Vista is restored, enter all exams into system. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | 1. Fire alarms needed to alert staff of a fire 2. Refrigeration: Refrigeration alarms being down may cause supplies to be lost. | Chief, Security Chief, Engineering Service |  | - By observing the monitors, etc. determine whether the alarm to the refrigeration is working. - Remain alert for notification via intercom on the fire alarm. | Manually monitor temperature within refrigerator. |
| 13. Elevators & Other Vertical Transport | Minimal Impact |  |  |  |  |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Delay in specimen testing/results. | Engineering Service |  | Contact Engineering service. | Physically walk specimens. |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | N/A | N/A | N/A | N/A | N/A |

DATE:      June 18, 2019

FUNCTIONAL UNIT:  P&LMS: Blood and Tissue Bank	 	         FUNCTIONAL UNIT MANAGER:  Angie McCowan-Bailey

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | OK with emergency. If no emergency light then could not read reactions to perform patient testing | Engineering | Have flashlights and fresh batteries on hand | Determine extent of outage | May relocate to area with better lighting |
| 2. Electrical Power (Generator Power Available) | OK with emergency. If loss of emergency power, Blood Bank would send patient testing to Kentucky Blood Center (KBC). We would not be able to perform patient testing. | Engineering | Use extension cords to connect critical equipment to emergency power outlets. | Length of downtime | May send patient testing to Kentucky Blood Center |
| 3. Steam Distribution | N/A | N/A | N/A | N/A | N/A |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Minimal Impact due to platelet and tissue incubator on emergency power. | Engineering | If no emergency power, all platelets would be sent back to KBC. Tissue implants would be moved to the stock room where the temperature is monitored | Determine extent of outage | If no emergency power, all platelets would be sent back to KBC. Tissue implants would be moved to the stock room where the temperature is monitored |
| 5. Room or Hood Exhaust | No Problems |  |  |  |  |
| 6. Water Delivery | Need to wash hands is critical | Safety Office | Use antibacterial hand cleanser. | Assess outage time. | Conserve and have additional (i.e., bottled) water available. |
| 7. Water Conditioning Or Drinkability | Minimal Impact | Supply Officer | If emergency power is available and water is available, we may use reagent grade water from our water purification system. |  |  |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Unable to dispose of cell washer waste | Safety Office | - Store waste in biohazard room until disposal can proceed. - Stock extra empty saline containers to handle waste overflow | Determine extent of outage | Contact Safety office for help with biohazard disposal. |
| 9. Critical Supplies | Would be unable to perform patient testing. | Chief, Supply and Purchasing | Store 2 week supply of critical reagents | Supply levels | - Keep enough in stock, borrow, or arrange with ordering company. - May need to send patient testing to KBC. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Unable to contact KBC for ordering blood. Also unable to contact OR and wards. Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | May need to have access to cellular phone to contact KBC. Landline located in blood bank above bench 20 and 21 | Determine extent of outage | - If computer is working, communicate via Outlook email - Hand deliver orders and communication to floors |
| 11. VISTA, VBECS, & Other Computer Applications | 1.Could not put orders for blood products or tissue implants in computer. 2. Could not use VBECS 3. An interruption in VISTA operations would interrupt order entry and results reporting. 4. Tissue implants would have to be recorded and tracked via paper instead of computer. 5. Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | 1. Would have to accept verbal orders by phone or use paper requisitions. 2. Use manual patient cards for recording patient typing and crossmatching reactions. | Determine extent of outage | Need phone service |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | All BB refrigerator, freezer, and platelet cabinet alarms are on emergency power. All tissue equipment is on emergency power. Fire alarm would be only problem. | Safety Officer | Manually watch and take temperatures every 4 hours on refrigerators, freezers, platelet cabinet, tissue cabinet and water bath if being used. | Determine extent of outage | - Inform staff. - Listen for intercom fire announcements. - Manually monitor temperature. |
| 13. Elevators & Other Vertical Transport | Minimal impact | Engineering | Specimens may not be able to get to lab or transport may not be able to pick blood up. | Determine extent of outage | Use the stairs instead of elevators. |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Minimal Impact | Engineering | Specimens may not be able to get to lab | Determine extent of outage | Transport samples or blood products via volunteer or technologist. |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | Not applicable |  |  |  |  |

DATE:     June 18, 2019

FUNCTIONAL UNIT:  P&LMS: Administrative Support	 		    FUNCTIONAL UNIT MANAGER:  Vicki Richardson

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Can work with emergency lighting | Engineering | Have flashlights and fresh batteries on hand | Determine extent of outage | May relocate to area with better lighting |
| 2. Electrical Power (Generator Power Available) | Can work with emergency power | Engineering | Use extension cords to connect critical equipment and water purification system to emergency power outlets. | Determine extent of outage | Cannot work without emergency power |
| 3. Steam Distribution | N/A |  |  |  |  |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Office heating or cooling needed | Engineering Service | Fans or heaters | Determine extent of outage | Fans and heaters may be acquired from Engineering to ensure operation of equipment |
| 5. Room or Hood Exhaust | N/A |  |  |  |  |
| 6. Water Delivery | Need to wash hands | Safety Office | Use antibacterial hand cleanser. | Assess outage time | Inventory hand cleanser |
| 7. Water Conditioning Or Drinkability | Drinking water availability | Supply Officer | If emergency power is available and water is available, we may use reagent grade water from our water purification system. | Minimize use | Minimize use |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | N/A |  |  |  |  |
| 9. Critical Supplies | Would be unable to perform service. | Chief, Supply and Purchasing | Try to keep adequate back supply | Supply levels | Keep enough in stock or borrow, or arrange with supply. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | 1. Could not call frozen sections 2. Could not use paging system 3. Would need to use landline phone for communication as other phone service is operated through Internet. | OI&T | Communicate verbally or via paper Landline located in blood bank above bench 20 and 21 | Assess for extent of outage | Communicate verbally or via paper |
| 11. VISTA & Other Computer Applications | 1. An interruption in VISTA operations would interrupt order entry and results reporting. 2. Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T | Type reports on paper | Assess for extent of outage. | Type reports on paper and enter in VISTA later. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Need to hear fire alarm | Safety Officer | 1. List for intercom message. 2. Verbal notification. | Assess extent of outage | 1. List for intercom message. 2. Verbal notification. |
| 13. Elevators & Other Vertical Transport | Minimal impact |  |  |  |  |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Minimal Impact |  |  |  |  |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | Minimal Impact |  |  |  |  |

DATE:       June 18, 2019

FUNCTIONAL UNIT:  P&LMS: Phlebotomy Laboratory 		         FUNCTIONAL UNIT MANAGER:  Michael Evans

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Without lights, phlebotomy would not be possible. | Safety Office | 1. Have flashlight with fresh batteries. 2. Inform staff of exit routes | 1. Extent of light failure should be evaluated. | - Move staff from dark to lighted area. - Maintain staff |
| 2. Electrical Power (Generator Power Available) | 1. Loss of primary source has little effect. 2. Loss of both primary and secondary, section may close. | Safety Office Engineering | Use extension cords to connect critical equipment and water purification system to emergency power outlets. | Service chief will assess and relay instructions. | Without power, section would close. |
| 3. Steam Distribution | N/A |  |  |  |  |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | 1. Loss of heat would impact staff (could not work in environment) 2. Overheating of room. | Engineering | Request fans from Engineering | Service chief will keep informed. | Move staff to appropriate area. |
| 5. Room or Hood Exhaust | N/A |  |  |  |  |
| 6. Water Delivery | 1. Hand washing critical. 2. Toilet will not flush | Safety Office | 1. Use antibacterial hand cleanser. 2. Check status of alternate restrooms (Rm. D-156) | 1. Service chief to keep updated. |  |
| 7. Water Conditioning Or Drinkability | Minimal impact |  | If emergency power is available and water is available, we may use reagent grade water from our water purification system. |  |  |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Would have to delay disposal of biohazardous waste | EMS | Store biohazardous waste in designated room in main laboratory until disposal is possible. | Volume of biohazardous waste | Notify EMS of need for assistance to pick up biohazardous waste. |
| 9. Critical Supplies | If extended, 2-3 weeks, warehouse supplies may become critical | Ware house Vendors | Keep enough supplies on hand for 2-3 weeks of testing | Evaluate as needed. | 1. Contact CDD 2. Contact area hospitals |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Loss of phones would impede communications between sections and hospital Would need to use landline phone for communication as other phone service is operated through Internet. | Chief of OI&T | Landline located in blood bank above bench 20 and 21 in B102 Cooper Drive |  | Use e-mail, if available |
| 11. VISTA & Other Computer Applications | 1. An interruption in VISTA operations would interrupt order entry and results reporting. 2. Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T LIM | Back up procedures are in place. | Wait for downtime length. | 1. Use miscellaneous slips for lab orders. 2. Outpatient back up collection list. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Fire alarms needed to alert of fire | Chief, Security | Alert staff that alarm system is down. |  | 1. Have staff listen to intercom for fire notice. 2. Dial 3600(LD) or 4500(CD) to report fire. |
| 13. Elevators & Other Vertical Transport | N/A |  |  |  |  |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Specimens would have to be walked over to main lab |  | Have personnel available to make deliveries as needed | Functioning of pneumatic tube | Deliver specimens as needed |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | N/A |  |  |  |  |

FUNCTIONAL UNIT:  Special Reference Lab - CDD	  								DATE:  June 18, 2019

FUNCTIONAL UNIT MANAGER: Kristina Kelley

| Mission Critical System | ##### Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of Critical system, then: Assess the situation for: Action required: |  |
| --- | --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | 1. Without lighting, staff can carry out limited duties. 2. Outside lights should be sufficient for egress | Safety Office | Stock flashlights and batteries | Determine extent and expected duration of outage. | 1. Staff may be asked to perform some tasks with lights from windows. 2. Staff may need to be transferred to labor pool. |
| 2. Electrical Power (Generator Power Available) | 1. Without power, staff cannot carry out their duties. 2. Power surges could damage equipment. | Safety Office Engineering | - Use extension cords to connect critical equipment and water purification system to emergency power outlets. - Manual tests could still be performed. - Determine other refrigerator space available for reagents. | SRL chief to determine extent of outage and projected length of outage. | 1. Staff will continue to do manual tests. 2. Some staff may need to be moved to labor pool. |
| 3. Steam Distribution | N/A |  |  |  |  |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | 1. Loss of heat may affect room temperature incubators. 2. Overheating could cause damage to electronic equipment. 3. Physical discomfort may prevent employees from being able to carry out duties. | Engineering Service | Request fans from engineering to help cool equipment; may be able to use incubators for R.T. incubations. | SRL chief to determine extent of the outage and projected length of the outage. | 1. Evaluate situation to protect equipment. 2. Wait until equipment cools down to restart testing. 3. Monitor room temperature. 4. May need to shift some employees to labor pool. |
| 5. Room or Hood Exhaust | N/A |  |  |  |  |
| 6. Water Delivery | 1. Water required for some tests. 2. Hand washing critical 3. Toilets would not function | Safety Office Engineering Service | 1. Carboys are available but not routinely used. They could be filled if advanced notice is given or water is available in research. 2. Use antibacterial hand cleanser. | SRL chief to determine extent and expected duration of outage. | 1. Inform staff to minimize water usage. 2. Call command center and provide status of operations. 3. Make arrangements for staff to use bathrooms elsewhere, if available. |
| 7. Water Conditioning Or Drinkability | 1. Minimal impact expect for drinking water. | Supply Officer Engineering Service | If emergency power is available and water is available, we may use reagent grade water from our water purification system. | SRL chief to determine extent of problem and expected duration. |  |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | 1. Unable to dispose of biohazard waste 2. Unable to flush toilets. | Safety Office |  | SRL chief to determine extent of problem and expected duration. | 1. Contact environmental management for assistance with disposal 2. Check on availability of rest rooms in another area. |
| 9. Critical Supplies | Unable to perform some tests if supplies not available. | SRL Supervisor Chief, Purchasing Chief, Fiscal | 1. Stock enough supplies to cover at least 2 weeks. 2. May require additional funding because of end-of-quarter shortages. | SRL chief to evaluate the situation and determine which assays can be performed. | 1. Check with main lab and other area labs to see if they can help. 2. Notify clients if tests cannot be done. |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Loss of phones will impede the SRL’s ability to communicate with client labs. Would need to use landline phone for communication as other phone service is operated through Internet. | Chief of OI&T | Landline located in blood bank above bench 20 and 21 | SRL chief to determine extent and projected length of outage and alternatives plans such as VISTA, mobile phones, and Microsoft Outlook. | 1. Continue to perform testing. 2. Use alternative communications, as possible, with clients. |
| 11. VISTA & Other Computer Applications | 1. An interruption in VISTA operations would interrupt order entry and results reporting. 2. Would need to use landline phone for communication. All other phones are dependent on internet connection. | OI&T Lab LIM | Establish backup system for accessioning specimens. | Lab LIM to determine extent and projected length of failure. | 1. Continue to perform assays 2. Manually accession specimens if downtime expected to be >24 hours. 3. FAX results to clients if downtime >24 hours. 4. Upon restoration of VISTA, accession specimens and enter results. |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Fire alarms needed to alert staff of a fire. | Chief, Security | Alert staff that alarm system is down. | 1. Chief, Security to alert staff that alarm is down. 2. Staff to respond as trained if fire situation occurs. |  |
| 13. Elevators & Other Vertical Transport | N/A. |  |  |  |  |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | N/A |  |  |  |  |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | N/A |  |  |  |  |

FUNCTIONAL UNIT:  P&LMS: Physical Security, Biological/Chemical Agent					DATE:  June 18, 2019

FUNCTIONAL UNIT MANAGER:   P&LMS Safety Officer, Section Supervisors

| Mission Critical System | Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | Assess the Situation For: | Action Required |
| --- | --- | --- | --- | --- | --- |
| HHS Select Agents | Unauthorized Use | VACO CDC USDA Police & Security Service | 1. Currently, no agents are being used. 2. Identification of any select agent or toxin will require reporting to CDC on APHIS/CDC form 4 to the proper authority (CDC/USDA) and meeting all requirements of laws governing their use and destruction, including the Patriot Act of 2002. | Continuously monitor Microbiology section for possession of HHS Select Agents. | 1. Notify proper authorities. 2. Maintain proper security of laboratory. |
| USDA-HHS Overlap Agents | Unauthorized Use | VACO CDC USDA Police & Security Service | 1. Currently, no agents are being used. 2. Identification of any select agent or toxin will require reporting to CDC on APHIS/CDC form 4 to the proper authority (CDC/USDA) and meeting all requirements of laws governing their use and destruction, including the Patriot Act of 2002. | Continuously monitor Microbiology section for possession of HHS Select Agents. | 1. Notify proper authorities. 2. Maintain proper security of laboratory |
| High Consequence Livestock Pathogens and Toxins | Unauthorized Use | VACO CDC USDA Police & Security Service | 1. Currently, no agents are being used. 2. Identification of any select agent or toxin will require reporting to CDC on APHIS/CDC form 4 to the proper authority (CDC/USDA) and meeting all requirements of laws governing their use and destruction, including the Patriot Act of 2002. | Continuously monitor Microbiology section for possession of HHS Select Agents. | 1. Notify proper authorities. 2. Maintain proper security of laboratory |

| Mission Critical System | Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | Assess the Situation For: | Action Required |
| --- | --- | --- | --- | --- | --- |
| Biological or Chemical Agents | Unauthorized Use | VACO CDC USDA Police & Security Service | 1. Currently, no agents are being used. 2. Identification of any select agent or toxin will require reporting on CDC form 0.1318 to the proper authority (CDC/USDA) and meeting all requirements of laws governing their use and destruction, including the Patriot Act of 2002. | Continuously monitor laboratory for possession of HHS Select Agents. | 1. Notify proper authorities. 2. Maintain proper security of laboratory |
| Non-Federal entities request for information on CDA, USDA, or VA biological or chemical agents | Use of information to be used to develop weapons of mass destruction | Chief, Police & Security Service | 1. Any request for literature that refers to biological or chemical agent and discusses their use as weapons of mass destruction in any way or techniques to improve their delivery or effectiveness will be immediately forwarded to the Chief, Police & Security Service. |  | 1. Policy needs to be reinforced to all P&LMS personnel during annual Safety Review. |
| Physical Security of Laboratory | Unauthorized Access to Laboratory | Chief, Police & Security Service | Laboratory is staffed 24 hours/day, 7days/week. Only authorized personnel with proper ID (VA, UK, and Sales Reps) are permitted in the laboratory. All entrances have PIV access locks that are PIV activated. All doors remain locked. Personnel requesting access must identify themselves via the intercom. | 1. Ensure that all doors to the laboratory are locked. 2. Employees on duty monitor personnel entering the laboratory other than P&LMS employees. | Notify Police & Security Service if any suspicious unauthorized personnel enter the laboratory. . Select agents identified must be kept in a locked space when not in use. Agents will be destroyed within seven (7) days of identification or transferred to a registered entity. |

Training Completion Certificate

By entering my signature below I confirm that I have read, understand, and accept the policy and procedure requirements detailed in the “Pathology and Laboratory Medicine Service Contingency Plan”

____________________________		_________________

SIGNATURE						DATE

_____________________________

Printed Name