Unsecured cylinder is a safety problem, it is lying horizontal, not upright, electrical cord in contact with the cylinder

Cylinders not protected from falling, chain not secured across

Electrical cord hanging, cylinder not secured

Cylinder not secured, combustibles stored with cylinders, bad housekeeping, Acetylene and Oxygen stored too close together and not chained off.

No safety cap, no valve, horizontal, subject to damage

Tank has suffered damage, take this cylinder out of service ASAP

Cylinders have decomposed/corroded. Should have been disposed of long ago.

Valve caps missing on two cylinders